## Read Me
Rooftop HVAC Plant Platform - Engineering Certification Checklist (Australia)
New building, metal roof. Chronological checklist with state and territory differences. Information as at 23 October 2026.
How to use
1. Open the 'Master Checklist' sheet and choose your state or territory in cell C2 (yellow).
2. Column J then shows the notes for that state. Columns K to R show every state side by side.
3. Work down the rows in order. Update Status, Owner and Due date (yellow columns); the progress cells at the top recalculate.
4. 'State Comparison' is a one-page quick reference; 'Sources & Verify' lists sources and what to confirm.
Colour key
Master Checklist: a state cell filled with that state's solid colour means the requirement DIFFERS from the national baseline. A grey cell reading 'Same as baseline' means no material difference.
State Comparison: each column uses a pale tint of the state colour, with the solid colour in the header.
Code | Jurisdiction | Colour | Colour name
QLD | Queensland |  | Maroon
NSW | New South Wales |  | Sky blue
VIC | Victoria |  | Dark blue (navy)
SA | South Australia |  | Red
WA | Western Australia |  | Gold
TAS | Tasmania |  | Forest green
NT | Northern Territory |  | Ochre
ACT | Australian Capital Territory |  | Lime green
Colours for QLD (maroon), NSW (sky blue) and VIC (dark blue) were specified by the requester; the other states use commonly associated colours and can be changed in the sheet.
Example of how to fill in the yellow columns
Item | Status | Owner | Due date
Structural design of the platform | In progress | J. Smith (structural engineer) | 15-Dec-2026 | Example only - not part of the checklist.
Scope and assumptions
Scope: engineering certification of a rooftop HVAC plant platform on a NEW building with a METAL roof (platform, access, roof structure, and the related approvals).
Baseline: the national position (NCC, AS/NZS 1170 series, AS 1657:2018, materials standards, model WHS framework). State columns show differences.
This is general information, not engineering or legal advice. The certifying engineer and building certifier decide the applicable codes, editions and certificates for a specific project.
Several items change quickly (NCC edition dates, engineer registration). See 'Sources & Verify' for the confidence level of each area.

## Master Checklist
Master Checklist - rooftop HVAC plant platform, new building, metal roof
| Project state: | QLD |  | Total items | 20
| Pick a state in C2: column J shows that state's notes. |  |  | Done | 0
| Yellow cells are for you to fill in. Coloured state cells = differs from baseline. |  |  | % complete (excl. N/A) | 0%
# | Stage | Requirement (national baseline) | Responsible party | Key standards / references (baseline) | Evidence / output | Status | Owner | Due date | Selected state: QLD | QLD | NSW | VIC | SA | WA | TAS | NT | ACT | Notes
1 | Pre-design | Check planning / development approval needs for rooftop plant (height, visual screening, noise) before building approval. | Architect / town planner | State planning legislation and local planning scheme; noise rules | Planning approval or exemption confirmation | Not started |  |  | Planning Act 2016 (Qld) and the local government planning scheme. | Planning Act 2016 (Qld) and the local government planning scheme. | Environmental Planning and Assessment Act 1979 (NSW) and Local Environmental Plan; DA or complying development pathway. | Planning and Environment Act 1987 (Vic) and local planning scheme; planning permit if required. | Planning, Development and Infrastructure Act 2016 (SA) and the Planning and Design Code (PlanSA). | Planning and Development Act 2005 (WA) and local planning scheme. | Land Use Planning and Approvals Act 1993 (Tas) and the Tasmanian Planning Scheme. | Planning Act 1999 (NT) and the NT Planning Scheme 2020. | Planning Act 2023 (ACT) and the Territory Plan.
2 | Pre-design | Confirm building class, importance level and which NCC edition applies at the date of application. | Certifier / structural engineer | NCC Vol 1 (Part A governing requirements, Section B structure); state variations | Design criteria statement | Not started |  |  | NCC 2022 (Amdts 1 and 2) mandatory until 30 Apr 2027; NCC 2025 from 1 May 2027. Queensland Development Code also applies. | NCC 2022 (Amdts 1 and 2) mandatory until 30 Apr 2027; NCC 2025 from 1 May 2027. Queensland Development Code also applies. | NCC 2022 until 30 Apr 2027; NCC 2025 from 1 May 2027. Edition is tied to when the construction certificate / CDC application is lodged. NSW variations apply. | NCC 2025 in force from 1 May 2026. Victorian variations apply. | Building Code: NCC 2022 Amdt 2 until 30 Apr 2027, then NCC 2025. (Plumbing Code 2025 already adopted 1 May 2026.) | NCC 2025 adopted 1 May 2026; most permit applications may use NCC 2022 (Amdts 1 and 2) until 30 Apr 2027. Mandatory from 1 May 2027. | NCC 2022 applies (reinstated 5 Jun 2026) until NCC 2025 from 1 May 2027. Sources conflict - confirm with CBOS Tasmania. | NCC 2025 reported as not adopted; NCC 2022 continues. Sources conflict - confirm with NT Building Control. | NCC 2025 commenced 1 May 2026; approvals before 1 May 2027 may use NCC 2022 + ACT 2022 Appendix or NCC 2025 + ACT 2025 Appendix.
3 | Pre-design | Determine wind region and terrain category, seismic hazard, snow (alpine sites) and corrosion environment for the site. | Structural engineer | AS/NZS 1170.2 (wind), AS 1170.4 (earthquake), AS/NZS 1170.3 (snow), AS/NZS 2312 (corrosion protection) | Site design criteria | Not started |  |  | Cyclonic Region C applies in parts of north Queensland - confirm region from the AS/NZS 1170.2 map for the actual site. | Cyclonic Region C applies in parts of north Queensland - confirm region from the AS/NZS 1170.2 map for the actual site. | Generally non-cyclonic; snow loads (AS/NZS 1170.3) apply in alpine areas; check coastal corrosion. | Generally non-cyclonic; snow loads apply in alpine areas. | Same as baseline. Generally non-cyclonic; confirm site seismic hazard and coastal corrosion. | Cyclonic Regions C and D apply in northern WA (Pilbara / Kimberley coast); Perth and the south are non-cyclonic. | Non-cyclonic; snow loads in highlands; exposed coastal or ridge sites need topographic multipliers. | Cyclonic Region C across the Top End (including Darwin); inland areas non-cyclonic. Allow for debris impact on platform screens. | Same as baseline. Non-cyclonic.
4 | Pre-design | Safe-design review: eliminate or minimise fall risk by design (guardrails over harness, plant set back from edges, clear access route, fragile surfaces). | Designers / principal designer / WHS lead | Model WHS Act designer duties; Safe Work Australia Managing the risk of falls at workplaces Code of Practice | Safe-design report / risk register | Not started |  |  | Same as baseline. WHS Act 2011 (Qld); regulator WorkSafe Queensland. | Same as baseline. WHS Act 2011 (Qld); regulator WorkSafe Queensland. | Same as baseline. WHS Act 2011 and WHS Regulation 2017 (NSW); regulator SafeWork NSW. | Not the model WHS law: OHS Act 2004 and OHS Regulations 2017 (Vic) apply, with designer duties; WorkSafe Victoria compliance codes and guidance apply instead of the SWA model code. | Same as baseline. WHS Act 2012 (SA); regulator SafeWork SA. | WHS Act 2020 and WHS (General) Regulations 2022 (WA); WA has its own Managing the risk of falls at workplaces Code of Practice; regulator WorkSafe WA. | Same as baseline. WHS Act 2012 (Tas); regulator WorkSafe Tasmania. | Same as baseline. WHS (National Uniform Legislation) Act 2011 (NT); regulator NT WorkSafe. | Same as baseline. WHS Act 2011 (ACT); regulator WorkSafe ACT.
5 | Design | Engage a suitably qualified engineer (CPEng / NER as a minimum benchmark) and confirm any statutory registration needed to certify. | Project manager / client | State engineer registration legislation; Engineers Australia credentials | Engineer appointment; registration number on certificates | Not started |  |  | Registered Professional Engineer of Queensland (RPEQ) required under the Professional Engineers Act 2002. | Registered Professional Engineer of Queensland (RPEQ) required under the Professional Engineers Act 2002. | Registration under the Design and Building Practitioners Act 2020 is compulsory for engineers on Class 2 buildings; not all engineers need registration for other work. | Registration under the Professional Engineers Registration Act 2019 (Vic) for prescribed areas (civil, structural, mechanical, electrical, fire safety) in the building industry. | No statutory registration scheme confirmed in sources reviewed (a scheme was under consultation) - confirm current status; use CPEng / NER. | Building engineering practitioner registration under the Building Services (Registration) Regulations 2011 (WA); phased start (structural / fire safety, then civil / mechanical) - confirm current status. | No dedicated statutory engineer registration scheme confirmed in sources reviewed - confirm with CBOS Tasmania; use CPEng / NER. | Engineers are registered by the NT Building Practitioners Board. | Professional Engineers Act 2023 (ACT): registration scheme started 6 Mar 2024 for civil, structural, mechanical, electrical and fire safety engineers.
6 | Design | Structural design of the platform: imposed loads (typically 2.5 or 5 kPa plus equipment weight), wind uplift / sliding / overturning, earthquake connections, deflection limits, materials. | Structural engineer | AS/NZS 1170.0, .1, .2, .4; AS 4100; AS/NZS 4600; AS/NZS 1664.1 (aluminium); AS 5216; AS/NZS 1554 | Calculations and structural drawings | Not started |  |  | Where in cyclonic Region C: add debris-impact and cyclic-load checks per AS/NZS 1170.2 and NCC cyclonic provisions. | Where in cyclonic Region C: add debris-impact and cyclic-load checks per AS/NZS 1170.2 and NCC cyclonic provisions. | Same as baseline. | Same as baseline. | Same as baseline. | Northern WA (Regions C / D): add debris-impact and cyclic-load checks; confirm region from the map. | Same as baseline. | Top End (Region C): cyclone-rated design, debris-impact and cyclic-load checks, including for screens and louvres. | Same as baseline.
7 | Design | Check the metal roof structure (purlins, rafters, primary frame) can carry platform and equipment reactions, and that load transfers to primary structure rather than sheeting. | Structural engineer | AS 4600; AS 4100; AS 1562.1 (metal roof sheeting); manufacturer data | Roof capacity assessment; framing and connection details | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.
8 | Design | Access and fall-prevention design: stairs, ladders, walkways, guardrails, toe boards, openings, edge protection and any anchor points. | Engineer / access designer | AS 1657:2018; NCC Vol 1; AS/NZS 1891.4; AS/NZS 5532; falls Code of Practice | Access and edge-protection drawings | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Follow WorkSafe Victoria fall-prevention guidance / compliance codes in place of the SWA model falls code. | Same as baseline. | Follow the WA Managing the risk of falls at workplaces Code of Practice. | Same as baseline. | Same as baseline. | Same as baseline.
9 | Design | If a proprietary platform system is used: obtain supplier engineering and test evidence and check it against site wind region, roof pitch, height and load limits. | Engineer / supplier | NCC Part A5 evidence of suitability; supplier certification | Product compliance data on file | Not started |  |  | Form 73 (Product technical statement) is available (non-mandatory) to document product compliance. | Form 73 (Product technical statement) is available (non-mandatory) to document product compliance. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.
10 | Approval | Lodge the building approval application with a certifier / permit authority and ensure the platform is in the approved documents. | Builder / certifier | State building legislation | Building approval / permit | Not started |  |  | Building Act 1975 (Qld); private certifier or council assesses the building work. | Building Act 1975 (Qld); private certifier or council assesses the building work. | Construction certificate from an accredited certifier (EP&A Act 1979) after DA consent or via a complying development certificate. | Building permit from a private or municipal building surveyor under the Building Act 1993 (Vic). | Development approval through PlanSA: planning consent plus building consent (council or accredited professional) under the PDI Act 2016. | Building permit under the Building Act 2011 (WA): certified application (with Certificate of Design Compliance) or uncertified via the permit authority. | Building Act 2016 (Tas): building surveyor pathway, including a Certificate of Likely Compliance, and building permit where required. | Building permit through a building certifier under the Building Act 1993 (NT). | Building approval through a certifier under the Building Act 2004 (ACT), including the ACT Appendix to the NCC.
11 | Approval | Engineer's design compliance certificate that the platform design meets the NCC and referenced standards. | Registered engineer | NCC Section B; AS/NZS 1170; AS 1657; material standards | Signed design certificate with calculations and drawings | Not started |  |  | Form 15 - Compliance certificate for building design or specification (RPEQ engineer). | Form 15 - Compliance certificate for building design or specification (RPEQ engineer). | Class 2 buildings: Design Compliance Declaration by a registered design practitioner under the DBP Act. Other classes: engineer's certificate accepted by the certifier. | Registered engineer's design certificate / computations lodged for the building permit. | Engineer's design certification / computations lodged with the building consent application. | Certificate of Design Compliance (CDC) for certified applications, supported by the engineer's certification. | Certificate of Likely Compliance (building surveyor) supported by the engineer's design certification. | Engineer's structural certification lodged with the building permit application. | Registered ACT engineer's design certification lodged with the building approval application.
12 | Pre-construction | Review shop drawings and material submissions (fixings, aluminium / steel grades, finishes, connections) against the engineer's design. | Contractor / engineer | AS 4100; AS/NZS 1664.1; AS/NZS 1554 or AS 1665 (welding) | Approved shop drawings | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.
13 | Construction | Safe work method statement and site safety plan for roof work (edge protection, fragile surfaces, rescue). | Installer / principal contractor | WHS Regulations (high-risk construction work); falls Code of Practice | SWMS, permits, toolbox records | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Equivalent duty sits in the Vic OHS Regulations 2017; follow WorkSafe Victoria guidance and compliance codes. | Same as baseline. | SWMS duty under the WHS (General) Regulations 2022 (WA); WA falls code applies. | Same as baseline. | Same as baseline. | Same as baseline.
14 | Construction | Install the platform (framing, fixings, anchors, roof penetrations and flashings) with engineer hold-point inspections. | Installer / engineer | Engineer's design; AS 1657; AS 1562.1 | Inspection records and photos | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.
15 | Construction | Install and test the access system: guardrails, ladders, stairs, edge protection and any anchors. | Installer | AS 1657; AS/NZS 1891.4; AS/NZS 5532 | Installation and test records | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.
16 | Completion | Engineer's inspection of the as-built platform and structural elements, and certification that it matches the design. | Registered engineer | Engineer's design; NCC Section B | Inspection / construction compliance certificate | Not started |  |  | Form 16 - Inspection certificate for building and structural elements (RPEQ engineer). | Form 16 - Inspection certificate for building and structural elements (RPEQ engineer). | Engineer's final inspection certificate to the certifier for the occupation certificate; Class 2 work follows the DBP Act regime (confirm scope). | Engineer's inspection / compliance certificate to the building surveyor ahead of final inspection. | Engineer's inspection / compliance certificate to the building certifier before the certificate of occupancy. | Certificate of Construction Compliance (CCC) for certified applications, supported by the engineer's certification. | Engineer's inspection certificate to the building surveyor to support completion. | Engineer's inspection certificate to the building certifier. | Engineer's inspection certification to the building certifier.
17 | Completion | Install and commission the HVAC equipment on the platform (supports, isolation, refrigerant and electrical connections). | Mechanical and electrical contractors | AS/NZS 5149; AS/NZS 3000; AS 1668; manufacturer instructions | Commissioning records; electrical compliance documentation | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.
18 | Completion | Final building certification / occupancy approval covering the building work. | Building certifier | State building legislation | Final certificate | Not started |  |  | Form 21 - Final inspection certificate (certifier). | Form 21 - Final inspection certificate (certifier). | Occupation Certificate (OC) under the EP&A Act 1979. | Certificate of final inspection or occupancy permit from the building surveyor (Building Act 1993). | Certificate of occupancy / completion under the PDI Act 2016, where required. | Occupancy permit or building approval certificate, with notice of completion, under the Building Act 2011. | Certificate of completion under the Building Act 2016. | Certificate of occupancy / completion under the Building Act 1993 (NT). | Certificate of occupancy and use under the Building Act 2004 (ACT).
19 | Handover | Hand over as-built drawings, calculations, O&M manuals and the anchor / access inspection regime. | Builder / engineer | AS 1851; AS/NZS 1891.4 | Handover pack | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.
20 | Operation | Periodic inspection and maintenance of the platform, guardrails, fixings, anchors and roof penetrations. | Owner / facility manager | AS 1851; AS/NZS 1891.4; WHS duties of a person conducting a business or undertaking | Maintenance log | Not started |  |  | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline. | Same as baseline.

## State Comparison
State Comparison - quick reference (rooftop HVAC platform, new building)
Indicative summary as at 23 Oct 2026. See 'Sources & Verify' for confidence levels.
Topic | QLD - Queensland | NSW - New South Wales | VIC - Victoria | SA - South Australia | WA - Western Australia | TAS - Tasmania | NT - Northern Territory | ACT - Australian Capital Territory
Planning law | Planning Act 2016 | EP&A Act 1979 (Local Environmental Plans) | Planning and Environment Act 1987 | PDI Act 2016 (Planning and Design Code) | Planning and Development Act 2005 | Land Use Planning and Approvals Act 1993 | Planning Act 1999 (NT Planning Scheme 2020) | Planning Act 2023 (Territory Plan)
Building law | Building Act 1975; Building Regulation 2021 | EP&A Act 1979 (certification); Building and Development Certifiers Act 2018 | Building Act 1993; Building Regulations 2018 | PDI Act 2016; PDI (General) Regulations 2017 | Building Act 2011; Building Regulations 2012 | Building Act 2016 | Building Act 1993 (NT) | Building Act 2004 (ACT)
NCC edition for building work (as researched Oct 2026) | NCC 2022 until 30 Apr 2027; NCC 2025 from 1 May 2027 | NCC 2022 until 30 Apr 2027; NCC 2025 from 1 May 2027 | NCC 2025 from 1 May 2026 | Building Code NCC 2022 to 30 Apr 2027, then NCC 2025; Plumbing Code 2025 from 1 May 2026 | NCC 2025 adopted 1 May 2026; either edition for most permits until 30 Apr 2027 | NCC 2022 until 1 May 2027 (sources conflict - verify) | NCC 2022 continues; NCC 2025 reported not adopted (verify) | NCC 2025 from 1 May 2026; either edition with ACT Appendix until 1 May 2027
Engineer registration | RPEQ (Professional Engineers Act 2002) | DBP Act 2020 - compulsory for Class 2 building work | Professional Engineers Registration Act 2019 | No scheme confirmed (was under consultation) | Building engineering practitioner registration (phased) | No dedicated scheme confirmed | NT Building Practitioners Board | Professional Engineers Act 2023 (from 6 Mar 2024)
Design certificate (typical) | Form 15 | Design Compliance Declaration (Class 2) / engineer certificate | Engineer design certificate with building permit | Engineer certification with building consent | Certificate of Design Compliance (CDC) | Certificate of Likely Compliance | Engineer structural certification | Engineer certification with building approval
Construction / inspection certificate (typical) | Form 16 | Engineer final inspection certificate | Engineer inspection certificate | Engineer inspection certificate | Certificate of Construction Compliance (CCC) | Engineer inspection certificate | Engineer inspection certificate | Engineer inspection certification
Final certificate (typical) | Form 21 Final inspection certificate | Occupation Certificate | Certificate of final inspection / occupancy permit | Certificate of occupancy / completion | Occupancy permit / building approval certificate | Certificate of completion | Certificate of occupancy / completion | Certificate of occupancy and use
WHS law | WHS Act 2011 (model) | WHS Act 2011 (model) | OHS Act 2004 (own framework) | WHS Act 2012 (model) | WHS Act 2020 (own version) | WHS Act 2012 (model) | WHS (National Uniform Legislation) Act 2011 (model) | WHS Act 2011 (model)
WHS regulator | WorkSafe Queensland | SafeWork NSW | WorkSafe Victoria | SafeWork SA | WorkSafe WA | WorkSafe Tasmania | NT WorkSafe | WorkSafe ACT
Falls guidance | Managing the risk of falls at workplaces Code of Practice | Managing the risk of falls at workplaces Code of Practice | WorkSafe Victoria compliance codes / guidance | Managing the risk of falls at workplaces Code of Practice | WA Managing the risk of falls at workplaces Code of Practice | Managing the risk of falls at workplaces Code of Practice | Managing the risk of falls at workplaces Code of Practice | Managing the risk of falls at workplaces Code of Practice
Wind / site hazard notes | Cyclonic Region C in parts of the north | Snow loads in alpine areas | Snow loads in alpine areas | Generally non-cyclonic | Cyclonic Regions C / D in the north | Snow in highlands; exposed sites | Top End cyclonic Region C | Generally non-cyclonic
State-specific code overlay | Queensland Development Code | NSW variations in NCC | Victorian variations in NCC | SA variations in NCC | WA variations in NCC | Tasmanian variations in NCC | NT appendix / variations | ACT Appendix to NCC

## Sources & Verify
Sources and items to verify
What to confirm, and how reliable each area is
Area | Basis | Confidence | Confirm with
NCC edition dates | Web research, 23 Oct 2026. Sources conflict on Tasmania, NT and ACT. | Medium | Building certifier / state building regulator before lodging
Engineer registration schemes | Web research for Qld, NSW, Vic, ACT, NT, WA. SA and Tas not confirmed. | Medium | State registration body; Engineers Australia
Certificate names and pathways outside Queensland | General knowledge of each state's building system; not individually verified. | Low to medium | Local certifier / building surveyor
Queensland Forms 15 and 16; Form 73 | Forms 15, 16 and Form 73 named in Qld Government newsflash list; Form 21 from general knowledge. | Medium | Queensland certifier
WHS framework differences (Vic, WA) | Web research and general knowledge; code titles and section references not checked. | Medium | WorkSafe Victoria; WorkSafe WA
Wind, snow and seismic site notes | General knowledge; the engineer must determine the actual region, terrain category and hazard factors for the site. | Low (indicative only) | Structural engineer
Standard editions (AS/NZS 1170.2:2021, AS 1657:2018 etc.) | Editions seen in supplier and industry sources; confirm current editions cited by the NCC edition in force. | Medium | Structural engineer
Sources consulted (web research, 23 Oct 2026)
Used for | Source | URL
NCC 2025 start in Queensland (1 May 2027) | Qld Government delayed-adoption notice | https://www.business.qld.gov.au/industries/building-property-development/building-construction/laws-codes-standards/delayed-adoption-ncc
Qld forms 12, 15, 16, 17, 18 amended; Form 73 product technical statement | Qld Government building and plumbing newsflash list | https://www.business.qld.gov.au/industries/building-property-development/building-construction/news/building-plumbing-newsflash
NCC 2025 adoption by jurisdiction | CPD On Demand - NCC 2025 vs NCC 2022 (state table) | https://cpdondemand.com.au/ncc-2025-vs-ncc-2022-what-changed-and-what-it-means-for-your-practice/
NCC 2025 adoption by jurisdiction | AEC Assistant - NCC 2025 adoption dates | https://www.aecassistant.com.au/news/ncc-2025-changes-state-adoption-dates
NCC 2025 adoption by jurisdiction (Tas / NT conflicts) | HIA - National Construction Code 2025 | https://hia.com.au/resources-and-advice/building-it-right/building-codes/national-construction-code-2025
WA NCC 2025 transition | AGWA - WA confirms NCC 2025 implementation | https://www.agwa.com.au/Web/Web/News/Articles/2026/Western-Australia-confirms-NCC-2025-implementation-and-transition-arrangements.aspx
Engineer registration by state | Engineers Australia - state registration | https://www.engineersaustralia.org.au/credentials/registration/state-registration
Engineer registration (NSW, Vic, Qld) | Clayton Utz - professional engineer regulation | https://claytonutz.com/insights/2022/july/keeping-up-with-the-changing-landscape-of-professional-engineers-registration-requirements
Engineer registration (ACT start 6 Mar 2024) | Pump Industry - professional engineer registration update | https://www.pumpindustry.com.au/professional-engineer-registration-an-update/
Engineer registration (WA phasing, SA consultation) | HVACR News - states move ahead on registration | https://hvacrnews.com.au/news/states-move-ahead-on-road-to-registration/
Model falls Code of Practice | Safe Work Australia | https://safeworkaustralia.gov.au/doc/model-code-practice-managing-risk-falls-workplaces
WA falls Code of Practice and WHS Act 2020 | WA Small Business Development Corporation licence finder | https://www.licence.smallbusiness.wa.gov.au/BusinessLicenceFinder/guided-search/fc4a4549-a7ac-4cfe-9a83-3cc5dda06b04/service/pid/18948
Platform standards used by suppliers (AS/NZS 1170, AS 1657, AS 1664.1) | NBS Source - EasyMech CR HVAC platform | https://source.thenbs.com/au/product/easymech-cr/xitfKk4ds8cwT9ygfTmscU
AS 1657:2018 scope and roof plan coordination | Safetylyne - roof plan design | https://www.safetylyne.com.au/roof-plan-design